## Corbel
CALCULATION NOTE
[8 empty] | NC |  | Activity Code |  |  | Material Code |  |  | Order No |  |  |  | Rev
[10 empty] | 9303 |  |  | 1733 |  |  | 005 |  |  |  | 0
Calculation of Reinforced Concrete Beam | [7 empty] | Issue |  | 0 | 1 |  | 2 | 3 |  | 4 |  | 5 |  | Page
[8 empty] | Date |  | 27/08/03
[8 empty] | Calculated |  | LC
[8 empty] | Checked |  | PC
File: RC Beam Design (ACI Code) Rev.0 | [7 empty] | Approved
| BENDING DESIGN | [10 empty] | CORBEL NO.
|  | 0.35 | 0.5
|  |  | 0.135 | [8 empty] | Beta1 |  |  |  | = | 0.85 |  |  |  |  | REBAR |  | A | Fy
[12 empty] | k = Beta1* 6120 / ( 6120 + fy ) | [9 empty] | DB | 10 | 0.785 | 4000
[12 empty] | k |  |  |  | = | 0.51403 |  |  |  |  | DB | 16 | 2.0096 | 4000
[12 empty] | m = fy/ 0.85f'c = | [5 empty] | 13.4454 |  |  |  | DB | 20 | 3.14 | 4000
[12 empty] | Phi |  |  |  | = | 0.9 |  |  |  |  | DB | 25 | 4.9062 | 4000
[12 empty] | u = Friction coefficient | [6 empty] | = | 1.4 |  | DB | 28 | 6.1544 | 4000
|  |  |  | 0.375 |  | 0.65 | [5 empty] | fy (kg/cm2) |  |  |  | = | 4000 |  |  |  |  | DB | 32 | 8.0384 | 4000
[6 empty] | a/d <1.0 OK | [5 empty] | f'c (ksc) |  |  |  | = | 350 |  |  |  |  | RB | 9 | 0.63585 | 2400
[6 empty] | B >0.5d O.K | [5 empty] | B (cm) |  |  |  | = | 30
[12 empty] | d (cm) |  |  |  | = | 37.5
[12 empty] | h (cm) |  |  |  | = | 40
As = Max of :
| 1 | Af +An |  | = | 7.1511 |  | cm^2
| 2 | 2/3(Avf)+An |  | = | 8.5945 |  | cm^2 |  |  |  |  | Min Nu =0.2Vu |  |  |  |  | = | 8.64 |  | Tons
| 3 | 0.04(fc'/fy)b*d |  | = | 3.9375 |  | cm^2 |  |  |  |  | Max Vu = min(0.2fc'bd , 56bd)
|  | As |  | = | 8.5945 |  | cm^2 | [7 empty] | 63000 |  |  |  | kg
| DB | [7 empty] | 3 |  |  | USE 3DB20
| Required number of rebar | [7 empty] | 3
Ah ( for closed stirrup) = Max of :
| 1 | 0.5Af |  | = | 2.3035 |  | cm^2
| 2 | 1/3Avf |  | = | 3.0857 |  | cm^2
|  | Ah |  | = | 3.0857 |  | cm^2 |  |  |  |  | Ah shall be placed with in 2d/3
| DB | [7 empty] | 1
| Required number of rebar | [7 empty] | 2 |  |  | USE 2DB10@8.4cm
| Maximun Ah spacing , (cm) | [7 empty] | 8.4 |  |  | Spacing shall < 10cm
CALCULATION
| Vu (Tons) | [7 empty] | 43.2 |  |  | Vu < Max Vu O.K
| Nu (Tons) | [7 empty] | 8.65
| Mu (Tons-m) = Vu*a+Nu*(h-d) | [7 empty] | 6.0483 |  |  | Nu >Min Nu O.K
| Ru = Mu/phi(bd^2) | [7 empty] | 15.9295
| p = (0.85fc'/fy)*(1-(1-2*Ru/0.85fc')^0.5) | [7 empty] | 0.0040951
| Af = p*b*d , (cm^2) | [7 empty] | 4.607
| DB | [7 empty] | 2
| Required number of rebar | [7 empty] | 3
| Actual p | [7 empty] | 0.0053589
| Phi Mn =Phi* p*fy*bd^2(1-0.59pfy/fc') , (Tons-m) | [7 empty] | 7.8448 |  |  | Phi Mn > Mu O.K
| An = Nu/(0.85*fy) , ( cm^2) | [7 empty] | 2.5441
| Avf = Vu/(0.85*u*fy) , (cm^2) | [7 empty] | 9.0756
1
1
Vuu
Nu
B
d
a
Ah
As

## Verify DR.Winit
CALCULATION NOTE
[8 empty] | NC |  | Activity Code |  |  | Material Code |  |  | Order No |  |  |  | Rev
TECHNIP ENGINEERING (THAILAND) LTD. | [9 empty] | 9303 |  |  | 1733 |  |  | 005 |  |  |  | 0
Calculation of Reinforced Concrete Beam | [7 empty] | Issue |  | 0 | 1 |  | 2 | 3 |  | 4 |  | 5 |  | Page
[8 empty] | Date |  | 27/08/03
[8 empty] | Calculated |  | LC
[8 empty] | Checked |  | PC
File: RC Beam Design (ACI Code) Rev.0 | [7 empty] | Approved
CORBEL NO.
|  | 0.35 | 0.2
|  |  | 0.135 | [8 empty] | Beta1 |  |  |  | = | 0.85 |  |  |  |  | REBAR |  | A | Fy
[12 empty] | k = Beta1* 6120 / ( 6120 + fy ) | [9 empty] | DB | 10 | 0.785 | 4000
[12 empty] | k |  |  |  | = | 0.51403 |  |  |  |  | DB | 16 | 2.0096 | 4000
[12 empty] | m = fy/ 0.85f'c = | [5 empty] | 13.4454 |  |  |  | DB | 20 | 3.14 | 4000
[12 empty] | Phi |  |  |  | = | 0.9 |  |  |  |  | DB | 25 | 4.9062 | 4000
[12 empty] | u = Friction coefficient | [6 empty] | = | 1.4 |  | DB | 28 | 6.1544 | 4000
|  |  |  | 0.375 |  | 0.4 | [5 empty] | fy (kg/cm2) |  |  |  | = | 4000 |  |  |  |  | DB | 32 | 8.0384 | 4000
[6 empty] | a/d <1.0 OK | [5 empty] | f'c (ksc) |  |  |  | = | 350 |  |  |  |  | RB | 9 | 0.63585 | 2400
[6 empty] | B >0.5d O.K | [5 empty] | B (cm) |  |  |  | = | 30
[12 empty] | d (cm) |  |  |  | = | 37.5
[12 empty] | h (cm) |  |  |  | = | 40
As = Max of :
| 1 | Af +An |  | = | 7.1511 |  | cm^2
| 2 | 2/3(Avf)+An |  | = | 8.5945 |  | cm^2 |  |  |  |  | Min Nu =0.2Vu |  |  |  |  | = | 8.64 |  | Tons
| 3 | 0.04(fc'/fy)b*d |  | = | 3.9375 |  | cm^2 |  |  |  |  | Max Vu = min(0.2fc'bd , 56bd)
|  | As |  | = | 8.5945 |  | cm^2 | [7 empty] | 63000 |  |  |  | kg
| DB | [7 empty] | 3 |  |  | USE 3DB20
| Required number of rebar | [7 empty] | 3
Ah ( for closed stirrup) = Max of :
| 1 | 0.5Af |  | = | 2.3035 |  | cm^2
| 2 | 1/3Avf |  | = | 3.0857 |  | cm^2
|  | Ah |  | = | 3.0857 |  | cm^2 |  |  |  |  | Ah shall be placed with in 2d/3
| DB | [7 empty] | 1
| Required number of rebar | [7 empty] | 2 |  |  | USE 2DB10@8.4cm
| Maximun Ah spacing , (cm) | [7 empty] | 8.4 |  |  | Spacing shall < 10cm
CALCULATION
| Vu (Tons) | [7 empty] | 43.2 |  |  | Vu < Max Vu O.K
| Nu (Tons) | [7 empty] | 8.65
| Mu (Tons-m) = Vu*a+Nu*(h-d) | [7 empty] | 6.0483 |  |  | Nu >Min Nu O.K
| Ru = Mu/phi(bd^2) | [7 empty] | 15.9295
| p = (0.85fc'/fy)*(1-(1-2*Ru/0.85fc')^0.5) | [7 empty] | 0.0040951
| Af = p*b*d , (cm^2) | [7 empty] | 4.607
| DB | [7 empty] | 2
| Required number of rebar | [7 empty] | 3
| Actual p | [7 empty] | 0.0053589
| Phi Mn =Phi* p*fy*bd^2(1-0.59pfy/fc') , (Tons-m) | [7 empty] | 7.8448 |  |  | Phi Mn > Mu O.K
| An = Nu/(0.85*fy) , ( cm^2) | [7 empty] | 2.5441
| Avf = Vu/(0.85*u*fy) , (cm^2) | [7 empty] | 9.0756
1
1
Vuuu
Nu
B
d
a
Ah
As
h