## YELLOW
Project |  |  | GFS | [7 empty] | Sheet No.
Subject |  |  | Discharge Load | [7 empty] | Project No.
| Design By |  |  | Narate |  |  | Checked by |  | Narate Meksook |  | Date |  | Feb, 09
Discharge Calculations Q1
Item |  | Details | Q1 | [8 empty] | Remarks
Reference
1 |  | Drainage Capacity to be Discharge Out
Actual I= 100mm/hr
1.1 |  | Surface Drainage Area A1 = |  |  |  |  | 2469 |  | m2
Dow uses 80mm/hr
1.2 |  | Rain Fall Intensity |  |  | I = | 150 |  | mm/hr. Return Peroid 5 years |  |  |  | Because site is so large |  | Noted :
[14 empty] | C = | 0.9 | For Roof
1.3 |  | Drainage Efficiency |  |  | C = | 85% |  | Flow efficiency | [5 empty] | C = | 0.85 | For Pavement Road
[14 empty] | C = | 0.25 | For Lawn
1.4 |  | Drainage Capacity Required Q i = A I C = | [6 empty] | 314.7975 | m3/hr.

## GREEN
Project |  |  | GFS | [7 empty] | Sheet No.
Subject |  |  | Discharge Load | [7 empty] | Project No.
| Design By |  |  | Narate |  |  | Checked by |  | Narate Meksook |  | Date |  | Feb, 09
Discharge Calculations Q1
Item |  | Details | Q1 | [8 empty] | Remarks
Reference
1 |  | Drainage Capacity to be Discharge Out
Actual I= 100mm/hr
1.1 |  | Surface Drainage Area A1 = |  |  |  |  | 6408 |  | m2
Dow uses 80mm/hr
1.2 |  | Rain Fall Intensity |  |  | I = | 100 |  | mm/hr. Return Peroid 5 years |  |  |  | Because site is so large |  | Noted :
[14 empty] | C = | 0.9 | For Roof
1.3 |  | Drainage Efficiency |  |  | C = | 85% |  | Flow efficiency | [5 empty] | C = | 0.85 | For Pavement Road
[14 empty] | C = | 0.25 | For Lawn
1.4 |  | Drainage Capacity Required Q i = A I C = | [6 empty] | 544.68 | m3/hr.

## Dark(1)
Project |  |  | GFS | [7 empty] | Sheet No.
Subject |  |  | Discharge Load | [7 empty] | Project No.
| Design By |  |  | Narate |  |  | Checked by |  | Narate Meksook |  | Date |  | Feb, 09
Discharge Calculations Q1
Item |  | Details | ROOF | [8 empty] | Remarks
Reference
1 |  | Drainage Capacity to be Discharge Out
Actual I= 100mm/hr
1.1 |  | Surface Drainage Area A1 = |  |  |  |  | 3186 |  | m2
Dow uses 80mm/hr
1.2 |  | Rain Fall Intensity |  |  | I = | 150 |  | mm/hr. Return Peroid 5 years |  |  |  | Because site is so large |  | Noted :
[14 empty] | C = | 0.9 | For Roof
1.3 |  | Drainage Efficiency |  |  | C = | 85% |  | Flow efficiency | [5 empty] | C = | 0.85 | For Pavement Road
[14 empty] | C = | 0.25 | For Lawn
1.4 |  | Drainage Capacity Required Q i = A I C = | [6 empty] | 406.215 | m3/hr.

## Dark (2)
Project |  |  | GFS | [7 empty] | Sheet No.
Subject |  |  | Discharge Load | [7 empty] | Project No.
| Design By |  |  | Narate |  |  | Checked by |  | Narate Meksook |  | Date |  | Feb, 09
Discharge Calculations Q1
Item |  | Details | GREEN | [8 empty] | Remarks
Reference
1 |  | Drainage Capacity to be Discharge Out
Actual I= 100mm/hr
1.1 |  | Surface Drainage Area A1 = |  |  |  |  | 1785 |  | m2
Dow uses 80mm/hr
1.2 |  | Rain Fall Intensity |  |  | I = | 150 |  | mm/hr. Return Peroid 5 years |  |  |  | Because site is so large |  | Noted :
[14 empty] | C = | 0.9 | For Roof
1.3 |  | Drainage Efficiency |  |  | C = | 25% |  | Flow efficiency | [5 empty] | C = | 0.85 | For Pavement Road
[14 empty] | C = | 0.25 | For Lawn
1.4 |  | Drainage Capacity Required Q i = A I C = | [6 empty] | 66.9375 | m3/hr.

## RED
Project |  |  | GFS | [7 empty] | Sheet No.
Subject |  |  | Discharge Load | [7 empty] | Project No.
| Design By |  |  | Narate |  |  | Checked by |  | Narate Meksook |  | Date |  | Feb, 09
Discharge Calculations Q1
Item |  | Details | ROOF | [8 empty] | Remarks
Reference
1 |  | Drainage Capacity to be Discharge Out
Actual I= 100mm/hr
1.1 |  | Surface Drainage Area A1 = |  |  |  |  | 2580 |  | m2
Dow uses 80mm/hr
1.2 |  | Rain Fall Intensity |  |  | I = | 150 |  | mm/hr. Return Peroid 5 years |  |  |  | Because site is so large |  | Noted :
[14 empty] | C = | 0.9 | For Roof
1.3 |  | Drainage Efficiency |  |  | C = | 85% |  | Flow efficiency | [5 empty] | C = | 0.85 | For Pavement Road
[14 empty] | C = | 0.25 | For Lawn
1.4 |  | Drainage Capacity Required Q i = A I C = | [6 empty] | 328.95 | m3/hr.

## Purple1
Project |  |  | GFS | [7 empty] | Sheet No.
Subject |  |  | Discharge Load | [7 empty] | Project No.
| Design By |  |  | Narate |  |  | Checked by |  | Narate Meksook |  | Date |  | Feb, 09
Discharge Calculations Q1
Item |  | Details | ROOF | [8 empty] | Remarks
Reference
1 |  | Drainage Capacity to be Discharge Out
Actual I= 100mm/hr
1.1 |  | Surface Drainage Area A1 = |  |  |  |  | 5000 |  | m2
Dow uses 80mm/hr
1.2 |  | Rain Fall Intensity |  |  | I = | 150 |  | mm/hr. Return Peroid 5 years |  |  |  | Because site is so large |  | Noted :
[14 empty] | C = | 0.9 | For Roof
1.3 |  | Drainage Efficiency |  |  | C = | 50% |  | Flow efficiency | [5 empty] | C = | 0.85 | For Pavement Road
[14 empty] | C = | 0.25 | For Lawn
1.4 |  | Drainage Capacity Required Q i = A I C = | [6 empty] | 375 | m3/hr.

## Blue
Project |  |  | GFS | [7 empty] | Sheet No.
Subject |  |  | Discharge Load | [7 empty] | Project No.
| Design By |  |  | Narate |  |  | Checked by |  | Narate Meksook |  | Date |  | Feb, 09
Discharge Calculations Q1
Item |  | Details | ROOF | [8 empty] | Remarks
Reference
1 |  | Drainage Capacity to be Discharge Out
Actual I= 100mm/hr
1.1 |  | Surface Drainage Area A1 = |  |  |  |  | 5000 |  | m2
Dow uses 80mm/hr
1.2 |  | Rain Fall Intensity |  |  | I = | 150 |  | mm/hr. Return Peroid 5 years |  |  |  | Because site is so large |  | Noted :
[14 empty] | C = | 0.9 | For Roof
1.3 |  | Drainage Efficiency |  |  | C = | 40% |  | Flow efficiency | [5 empty] | C = | 0.85 | For Pavement Road
[14 empty] | C = | 0.25 | For Lawn
1.4 |  | Drainage Capacity Required Q i = A I C = | [6 empty] | 300 | m3/hr.
1.1

## Blue (2)
Project |  |  | GFS | [7 empty] | Sheet No.
Subject |  |  | Discharge Load | [7 empty] | Project No.
| Design By |  |  | Narate |  |  | Checked by |  | Narate Meksook |  | Date |  | Feb, 09
Discharge Calculations Q1
Item |  | Details | ROOF | [8 empty] | Remarks
Reference
1 |  | Drainage Capacity to be Discharge Out
Actual I= 100mm/hr
1.1 |  | Surface Drainage Area A1 = |  |  |  |  | 4027 |  | m2
Dow uses 80mm/hr
1.2 |  | Rain Fall Intensity |  |  | I = | 150 |  | mm/hr. Return Peroid 5 years |  |  |  | Because site is so large |  | Noted :
[14 empty] | C = | 0.9 | For Roof
1.3 |  | Drainage Efficiency |  |  | C = | 40% |  | Flow efficiency | [5 empty] | C = | 0.85 | For Pavement Road
[14 empty] | C = | 0.25 | For Lawn
1.4 |  | Drainage Capacity Required Q i = A I C = | [6 empty] | 241.62 | m3/hr.

## Blue (3)
Project |  |  | GFS | [7 empty] | Sheet No.
Subject |  |  | Discharge Load | [7 empty] | Project No.
| Design By |  |  | Narate |  |  | Checked by |  | Narate Meksook |  | Date |  | Feb, 09
Discharge Calculations Q1
Item |  | Details | ROOF | [8 empty] | Remarks
Reference
1 |  | Drainage Capacity to be Discharge Out
Actual I= 100mm/hr
1.1 |  | Surface Drainage Area A1 = |  |  |  |  | 2574 |  | m2
Dow uses 80mm/hr
1.2 |  | Rain Fall Intensity |  |  | I = | 150 |  | mm/hr. Return Peroid 5 years |  |  |  | Because site is so large |  | Noted :
[14 empty] | C = | 0.9 | For Roof
1.3 |  | Drainage Efficiency |  |  | C = | 90% |  | Flow efficiency | [5 empty] | C = | 0.85 | For Pavement Road
[14 empty] | C = | 0.25 | For Lawn
1.4 |  | Drainage Capacity Required Q i = A I C = | [6 empty] | 347.49 | m3/hr.

## end
Project |  |  | GFS | [7 empty] | Sheet No.
Subject |  |  | Discharge Load | [7 empty] | Project No.
| Design By |  |  | Narate |  |  | Checked by |  | Narate Meksook |  | Date |  | Feb, 09
Discharge Calculations Q1
Item |  | Details | ROOF | [8 empty] | Remarks
Reference
1 |  | Drainage Capacity to be Discharge Out
Actual I= 100mm/hr
1.1 |  | Surface Drainage Area A1 = |  |  |  |  | 2574 |  | m2
Dow uses 80mm/hr
1.2 |  | Rain Fall Intensity |  |  | I = | 150 |  | mm/hr. Return Peroid 5 years |  |  |  | Because site is so large |  |  | Noted :
[15 empty] | C = | 0.9 | For Roof
1.3 |  | Drainage Efficiency |  |  | C = | 85% |  | Flow efficiency | [6 empty] | C = | 0.85 | For Pavement Road
[15 empty] | C = | 0.25 | For Lawn
1.4 |  | Drainage Capacity Required Q i = A I C = | [6 empty] | 328.185 | m3/hr. |  |  |  | 722

## gravel
Project |  |  | GFS | [7 empty] | Sheet No.
Subject |  |  | Discharge Load | [7 empty] | Project No.
| Design By |  |  | Narate |  |  | Checked by |  | Narate Meksook |  | Date |  | Feb, 09
Discharge Calculations Q1
Item |  | Details | ROOF | [8 empty] | Remarks
Reference
1 |  | Drainage Capacity to be Discharge Out
Actual I= 100mm/hr
1.1 |  | Surface Drainage Area A1 = |  |  |  |  | 5520 |  | m2
Dow uses 80mm/hr
1.2 |  | Rain Fall Intensity |  |  | I = | 150 |  | mm/hr. Return Peroid 5 years |  |  |  | Because site is so large |  |  | Noted :
[15 empty] | C = | 0.9 | For Roof
1.3 |  | Drainage Efficiency |  |  | C = | 25% |  | Flow efficiency | [6 empty] | C = | 0.85 | For Pavement Road
[15 empty] | C = | 0.25 | For Lawn
1.4 |  | Drainage Capacity Required Q i = A I C = | [6 empty] | 207 | m3/hr. |  |  |  | 722

## Gutter 1
Project |  |  |  | Haffale | [11 empty] | Sheet No.
Subject |  |  |  | Site Drainage Routes A5 | [11 empty] | Project No.
| Design By |  |  |  | Narate |  |  | Checked by |  |  | Jadsada |  |  |  |  | Date |  | Feb, 09
Summary Rectangular Drainage Calculations
Item |  | Details | [14 empty] | Remarks
Reference
1
+
+
+
[19 empty] | + | [5 empty] | Noted :
[19 empty] | + | [5 empty] | C = | 0.9 | For Roof
[19 empty] | + | [5 empty] | C = | 0.85 | For Pavement Road
[25 empty] | C = | 0.25 | For Lawn
|  | Drainage Capacity Required Q i = A I C = | [8 empty] | 314.7975 |  |  | m3/hr.
2 |  | Gutter Discharge Capacity Calcalations
|  |  |  | Manning Equations : |  |  |  |  | Qo= | (1/h)AR2/3S1/2
|  |  |  | When : |  | h : | Rougheness Surface Coefficient
[6 empty] | h = | 0.016 For concrete or asphaltic orcast Iron
[6 empty] | h = | 0.009 For pvc or glass or plastic
[6 empty] | h = | 0.012 For welded steel and wrought Iron
[6 empty] | h = | 0.015 For cast Iron uncoated pipe
[6 empty] | h = | 0.024 For corrugate metal sheet
[6 empty] | h = | 0.011 For asbestos
2.1 |  |  | Input |  | h = | 0.016
4.65
2.2 |  |  | Gutter Width b = |  |  |  | 400 |  |  | Gutter Total Depth d = |  |  |  |  | 400 |  |  |  |  | 2.325 | 0.625
[22 empty] | -2.3 |  | 0.6
2.3 |  |  | Pipe Slope 1 : |  |  | 500 | [15 empty] | -1.7 |  | 0.342
[17 empty] | free broad=50mm. |  |  |  |  | -1.4
2.4 |  |  | Assume Q max |  |  | when Normal Depth y n |  |  |  |  | = | 350 |  |  |  |  | then yn=d-50mm. |  |  |  |  | -0.9
2.5 |  |  | Surface Width |  |  | B = | 400 |  |  |  | or B = |  | 0.4 |  | m.
2.6 |  |  | Gutter Discharge Cross-Area A = | [6 empty] | 0.14 |  | m2
2.7 |  |  | Wetted Perimeter W = |  |  |  |  | 1.1 |  | m.
2.8 |  |  | Hydrualic Radius R = |  |  |  |  | 0.12727 |  | m.
2.9 |  |  | Discharge Capacity Q 0 = | [6 empty] | 0.09901 |  | m3/sec.
2.1 |  |  | Discharge Velocity Vo = | [5 empty] | 0.70722 |  | m/sec. |  |  |  |  | ok. | > 0.60 m/s OK
2.11 |  |  | Safety Factor S.F.= |  |  |  | 1
2.12 |  | Gutter Discharge "Net Capacity" Q n= | [7 empty] | 356.4367 |  | m3/hr.
[10 empty] | > | Q i= | 314.7975 |  | m3/hr. |  | ok. | [6 empty] | 5220
3 |  | Check critical depth for Hydrualic jump Qc | [8 empty] | from Qc2 = A3g / B
or yc=(Q02*B/g)^(1/3)/b
3.1 |  | Calculations Qc = |  |  |  | 0.25934 |  | m3/sec. |  | > | Q0= | 0.09901 |  | m3/sec. |  | ok.
|  | Calculations yc = |  |  |  | 0.1842 |  | m. |  | < | yn= | 0.35 |  | m. |  | ok.
3.2 |  | Noted :
|  |  |  | Qc | = | Q0 |  | Then Critical-flow
|  |  | or | ( yc | = | yn )
|  |  |  | Qc | > | Q0 |  | Then Sub-Critical-flow | [5 empty] | "Preferable"
|  |  | or | ( yc | < | yn )
|  |  |  | Qc | < | Q0 |  | Then Supper-Critical-flow
|  |  | or | ( yc | > | yn )

## Gutter2
Project |  |  |  | Haffale | [11 empty] | Sheet No.
Subject |  |  |  | Site Drainage Routes A5 | [11 empty] | Project No.
| Design By |  |  |  | Narate |  |  | Checked by |  |  | Jadsada |  |  |  |  | Date |  | Feb, 09
Summary Rectangular Drainage Calculations
Item |  | Details | [14 empty] | Remarks
Reference
1
+
+
+
[19 empty] | + | Area roof &Road = | 11594 | C1 | 0.9 | Noted :
[19 empty] | + | Area roof2 = |  | C2 | 0.9 | C = | 0.9 | For Roof
[19 empty] | + | Area Road1 = |  | C3 | 0.85 | C = | 0.85 | For Pavement Road
[20 empty] | Area Road2 = |  | C4 | 0.85 | C = | 0.25 | For Lawn
|  | Drainage Capacity Required Q i = A I C = | [8 empty] | 544.68 |  |  | m3/hr.
2 |  | Gutter Discharge Capacity Calcalations
|  |  |  | Manning Equations : |  |  |  |  | Qo= | (1/h)AR2/3S1/2
|  |  |  | When : |  | h : | Rougheness Surface Coefficient
[6 empty] | h = | 0.016 For concrete or asphaltic orcast Iron
[6 empty] | h = | 0.009 For pvc or glass or plastic
[6 empty] | h = | 0.012 For welded steel and wrought Iron
[6 empty] | h = | 0.015 For cast Iron uncoated pipe
[6 empty] | h = | 0.024 For corrugate metal sheet
[6 empty] | h = | 0.011 For asbestos
2.1 |  |  | Input |  | h = | 0.016
2.2 |  |  | Gutter Width b = |  |  |  | 400 |  |  | Gutter Total Depth d = |  |  |  |  | 650
2.3 |  |  | Pipe Slope 1 : |  |  | 500
free broad=50mm.
2.4 |  |  | Assume Q max |  |  | when Normal Depth y n |  |  |  |  | = | 600 |  |  |  |  | then yn=d-50mm.
2.5 |  |  | Surface Width |  |  | B = | 400 |  |  |  | or B = |  | 0.4 |  | m.
2.6 |  |  | Gutter Discharge Cross-Area A = | [6 empty] | 0.24 |  | m2
2.7 |  |  | Wetted Perimeter W = |  |  |  |  | 1.6 |  | m.
2.8 |  |  | Hydrualic Radius R = |  |  |  |  | 0.15 |  | m. | [10 empty] | 5928
2.9 |  |  | Discharge Capacity Q 0 = | [6 empty] | 0.18938 |  | m3/sec.
2.1 |  |  | Discharge Velocity Vo = | [5 empty] | 0.78908 |  | m/sec. |  |  |  |  | ok. | > 0.60 m/s OK
2.11 |  |  | Safety Factor S.F.= |  |  |  | 1
2.12 |  | Gutter Discharge "Net Capacity" Q n= | [7 empty] | 681.7675 |  | m3/hr.
[10 empty] | > | Q i= | 544.68 |  | m3/hr. |  | ok.
3 |  | Check critical depth for Hydrualic jump Qc | [8 empty] | from Qc2 = A3g / B
[11 empty] | or yc=(Q02*B/g)^(1/3)/b | [10 empty] | -0.9
1300
3.1 |  | Calculations Qc = |  |  |  | 0.58209 |  | m3/sec. |  | > | Q0= | 0.18938 |  | m3/sec. |  | ok. | [5 empty] | 650
|  | Calculations yc = |  |  |  | 0.28382 |  | m. |  | < | yn= | 0.6 |  | m. |  | ok.
3.2 |  | Noted :
|  |  |  | Qc | = | Q0 |  | Then Critical-flow
|  |  | or | ( yc | = | yn )
|  |  |  | Qc | > | Q0 |  | Then Sub-Critical-flow | [5 empty] | "Preferable"
|  |  | or | ( yc | < | yn )
|  |  |  | Qc | < | Q0 |  | Then Supper-Critical-flow
|  |  | or | ( yc | > | yn )

## Gutter3
Project |  |  |  | Haffale | [11 empty] | Sheet No.
Subject |  |  |  | Site Drainage Routes A5 | [11 empty] | Project No.
| Design By |  |  |  | Narate |  |  | Checked by |  |  | Jadsada |  |  |  |  | Date |  | Feb, 09
Summary Rectangular Drainage Calculations
Item |  | Details | [14 empty] | Remarks
Reference
1
+
+
+
[19 empty] | + | Area roof &Road = | 11594 | C1 | 0.9 | Noted :
[19 empty] | + | Area roof2 = |  | C2 | 0.9 | C = | 0.9 | For Roof
[19 empty] | + | Area Road1 = |  | C3 | 0.85 | C = | 0.85 | For Pavement Road
[20 empty] | Area Road2 = |  | C4 | 0.85 | C = | 0.25 | For Lawn
|  | Drainage Capacity Required Q i = A I C = | [8 empty] | 473.1525 |  |  | m3/hr.
2 |  | Gutter Discharge Capacity Calcalations
|  |  |  | Manning Equations : |  |  |  |  | Qo= | (1/h)AR2/3S1/2
|  |  |  | When : |  | h : | Rougheness Surface Coefficient
[6 empty] | h = | 0.016 For concrete or asphaltic orcast Iron
[6 empty] | h = | 0.009 For pvc or glass or plastic
[6 empty] | h = | 0.012 For welded steel and wrought Iron
[6 empty] | h = | 0.015 For cast Iron uncoated pipe
[6 empty] | h = | 0.024 For corrugate metal sheet
[6 empty] | h = | 0.011 For asbestos
2.1 |  |  | Input |  | h = | 0.016
2.2 |  |  | Gutter Width b = |  |  |  | 400 |  |  | Gutter Total Depth d = |  |  |  |  | 450
2.3 |  |  | Pipe Slope 1 : |  |  | 500
free broad=50mm.
2.4 |  |  | Assume Q max |  |  | when Normal Depth y n |  |  |  |  | = | 400 |  |  |  |  | then yn=d-50mm.
2.5 |  |  | Surface Width |  |  | B = | 400 |  |  |  | or B = |  | 0.4 |  | m.
2.6 |  |  | Gutter Discharge Cross-Area A = | [6 empty] | 0.16 |  | m2
2.7 |  |  | Wetted Perimeter W = |  |  |  |  | 1.2 |  | m.
2.8 |  |  | Hydrualic Radius R = |  |  |  |  | 0.13333 |  | m.
2.9 |  |  | Discharge Capacity Q 0 = | [6 empty] | 0.11672 |  | m3/sec.
2.1 |  |  | Discharge Velocity Vo = | [5 empty] | 0.72949 |  | m/sec. |  |  |  |  | ok. | > 0.60 m/s OK
2.11 |  |  | Safety Factor S.F.= |  |  |  | 1
2.12 |  | Gutter Discharge "Net Capacity" Q n= | [7 empty] | 420.1877 |  | m3/hr.
[10 empty] | > | Q i= | 473.1525 |  | m3/hr. |  | Not ok.
3 |  | Check critical depth for Hydrualic jump Qc | [8 empty] | from Qc2 = A3g / B
[11 empty] | or yc=(Q02*B/g)^(1/3)/b | [10 empty] | -0.9
1300
3.1 |  | Calculations Qc = |  |  |  | 0.31685 |  | m3/sec. |  | > | Q0= | 0.11672 |  | m3/sec. |  | ok. | [5 empty] | 650
|  | Calculations yc = |  |  |  | 0.20555 |  | m. |  | < | yn= | 0.4 |  | m. |  | ok.
3.2 |  | Noted :
|  |  |  | Qc | = | Q0 |  | Then Critical-flow
|  |  | or | ( yc | = | yn )
|  |  |  | Qc | > | Q0 |  | Then Sub-Critical-flow | [5 empty] | "Preferable"
|  |  | or | ( yc | < | yn )
|  |  |  | Qc | < | Q0 |  | Then Supper-Critical-flow
|  |  | or | ( yc | > | yn )

## RED1
Project |  |  |  | Haffale | [11 empty] | Sheet No.
Subject |  |  |  | Site Drainage Routes A5 | [11 empty] | Project No.
| Design By |  |  |  | Narate |  |  | Checked by |  |  | Jadsada |  |  |  |  | Date |  | Feb, 09
Summary Rectangular Drainage Calculations
Item |  | Details | [14 empty] | Remarks
Reference
1
+
+
+
[19 empty] | + | Area roof &Road = | 11594 | C1 | 0.9 | Noted :
[19 empty] | + | Area roof2 = |  | C2 | 0.9 | C = | 0.9 | For Roof
[19 empty] | + | Area Road1 = |  | C3 | 0.85 | C = | 0.85 | For Pavement Road
[20 empty] | Area Road2 = |  | C4 | 0.85 | C = | 0.25 | For Lawn
|  | Drainage Capacity Required Q i = A I C = | [8 empty] | 802.1025 |  |  | m3/hr.
2 |  | Gutter Discharge Capacity Calcalations
|  |  |  | Manning Equations : |  |  |  |  | Qo= | (1/h)AR2/3S1/2
|  |  |  | When : |  | h : | Rougheness Surface Coefficient
[6 empty] | h = | 0.016 For concrete or asphaltic orcast Iron
[6 empty] | h = | 0.009 For pvc or glass or plastic
[6 empty] | h = | 0.012 For welded steel and wrought Iron
[6 empty] | h = | 0.015 For cast Iron uncoated pipe
[6 empty] | h = | 0.024 For corrugate metal sheet
[6 empty] | h = | 0.011 For asbestos
2.1 |  |  | Input |  | h = | 0.016
2.2 |  |  | Gutter Width b = |  |  |  | 400 |  |  | Gutter Total Depth d = |  |  |  |  | 750
2.3 |  |  | Pipe Slope 1 : |  |  | 500
free broad=50mm.
2.4 |  |  | Assume Q max |  |  | when Normal Depth y n |  |  |  |  | = | 700 |  |  |  |  | then yn=d-50mm.
2.5 |  |  | Surface Width |  |  | B = | 400 |  |  |  | or B = |  | 0.4 |  | m.
2.6 |  |  | Gutter Discharge Cross-Area A = | [6 empty] | 0.28 |  | m2
2.7 |  |  | Wetted Perimeter W = |  |  |  |  | 1.8 |  | m.
2.8 |  |  | Hydrualic Radius R = |  |  |  |  | 0.15556 |  | m. | [10 empty] | 5928
2.9 |  |  | Discharge Capacity Q 0 = | [6 empty] | 0.22637 |  | m3/sec.
2.1 |  |  | Discharge Velocity Vo = | [5 empty] | 0.80845 |  | m/sec. |  |  |  |  | ok. | > 0.60 m/s OK |  |  |  |  | 120
2.11 |  |  | Safety Factor S.F.= |  |  |  | 1
2.12 |  | Gutter Discharge "Net Capacity" Q n= | [7 empty] | 814.9155 |  | m3/hr.
[10 empty] | > | Q i= | 802.1025 |  | m3/hr. |  | ok.
3 |  | Check critical depth for Hydrualic jump Qc | [8 empty] | from Qc2 = A3g / B
[11 empty] | or yc=(Q02*B/g)^(1/3)/b | [10 empty] | -0.9
1300
3.1 |  | Calculations Qc = |  |  |  | 0.73351 |  | m3/sec. |  | > | Q0= | 0.22637 |  | m3/sec. |  | ok. | [5 empty] | 650
|  | Calculations yc = |  |  |  | 0.31967 |  | m. |  | < | yn= | 0.7 |  | m. |  | ok.
3.2 |  | Noted :
|  |  |  | Qc | = | Q0 |  | Then Critical-flow
|  |  | or | ( yc | = | yn )
|  |  |  | Qc | > | Q0 |  | Then Sub-Critical-flow | [5 empty] | "Preferable"
|  |  | or | ( yc | < | yn )
|  |  |  | Qc | < | Q0 |  | Then Supper-Critical-flow
|  |  | or | ( yc | > | yn )

## purple
Project |  |  |  | Haffale | [11 empty] | Sheet No.
Subject |  |  |  | Site Drainage Routes A5 | [11 empty] | Project No.
| Design By |  |  |  | Narate |  |  | Checked by |  |  | Jadsada |  |  |  |  | Date |  | Feb, 09
Summary Rectangular Drainage Calculations
Item |  | Details | [14 empty] | Remarks
Reference
1
+
+
+
[19 empty] | + | Area roof &Road = | 11594 | C1 | 0.9 | Noted :
[19 empty] | + | Area roof2 = |  | C2 | 0.9 | C = | 0.9 | For Roof
[19 empty] | + | Area Road1 = |  | C3 | 0.85 | C = | 0.85 | For Pavement Road
[20 empty] | Area Road2 = |  | C4 | 0.85 | C = | 0.25 | For Lawn
|  | Drainage Capacity Required Q i = A I C = | [8 empty] | 375 |  |  | m3/hr.
2 |  | Gutter Discharge Capacity Calcalations
|  |  |  | Manning Equations : |  |  |  |  | Qo= | (1/h)AR2/3S1/2
|  |  |  | When : |  | h : | Rougheness Surface Coefficient
[6 empty] | h = | 0.016 For concrete or asphaltic orcast Iron
[6 empty] | h = | 0.009 For pvc or glass or plastic
[6 empty] | h = | 0.012 For welded steel and wrought Iron
[6 empty] | h = | 0.015 For cast Iron uncoated pipe
[6 empty] | h = | 0.024 For corrugate metal sheet
[6 empty] | h = | 0.011 For asbestos
2.1 |  |  | Input |  | h = | 0.016
2.2 |  |  | Gutter Width b = |  |  |  | 400 |  |  | Gutter Total Depth d = |  |  |  |  | 425
2.3 |  |  | Pipe Slope 1 : |  |  | 500
free broad=50mm.
2.4 |  |  | Assume Q max |  |  | when Normal Depth y n |  |  |  |  | = | 375 |  |  |  |  | then yn=d-50mm.
2.5 |  |  | Surface Width |  |  | B = | 400 |  |  |  | or B = |  | 0.4 |  | m.
2.6 |  |  | Gutter Discharge Cross-Area A = | [6 empty] | 0.15 |  | m2
2.7 |  |  | Wetted Perimeter W = |  |  |  |  | 1.15 |  | m.
2.8 |  |  | Hydrualic Radius R = |  |  |  |  | 0.13043 |  | m. | [9 empty] | 375 | 5928
2.9 |  |  | Discharge Capacity Q 0 = | [6 empty] | 0.10783 |  | m3/sec.
2.1 |  |  | Discharge Velocity Vo = | [5 empty] | 0.71888 |  | m/sec. |  |  |  |  | ok. | > 0.60 m/s OK |  |  |  |  | 120
2.11 |  |  | Safety Factor S.F.= |  |  |  | 1
2.12 |  | Gutter Discharge "Net Capacity" Q n= | [7 empty] | 388.196 |  | m3/hr.
[10 empty] | > | Q i= | 375 |  | m3/hr. |  | ok.
3 |  | Check critical depth for Hydrualic jump Qc | [8 empty] | from Qc2 = A3g / B
[11 empty] | or yc=(Q02*B/g)^(1/3)/b | [10 empty] | -0.9
1300
3.1 |  | Calculations Qc = |  |  |  | 0.28761 |  | m3/sec. |  | > | Q0= | 0.10783 |  | m3/sec. |  | ok. | [5 empty] | 650
|  | Calculations yc = |  |  |  | 0.19498 |  | m. |  | < | yn= | 0.375 |  | m. |  | ok.
3.2 |  | Noted :
|  |  |  | Qc | = | Q0 |  | Then Critical-flow
|  |  | or | ( yc | = | yn )
|  |  |  | Qc | > | Q0 |  | Then Sub-Critical-flow | [5 empty] | "Preferable"
|  |  | or | ( yc | < | yn )
|  |  |  | Qc | < | Q0 |  | Then Supper-Critical-flow
|  |  | or | ( yc | > | yn )

## Blue1
Project |  |  |  | Haffale | [11 empty] | Sheet No.
Subject |  |  |  | Site Drainage Routes A5 | [11 empty] | Project No.
| Design By |  |  |  | Narate |  |  | Checked by |  |  | Jadsada |  |  |  |  | Date |  | Feb, 09
Summary Rectangular Drainage Calculations
Item |  | Details | [14 empty] | Remarks
Reference
1
+
+
+
[19 empty] | + | Area roof &Road = | 11594 | C1 | 0.9 | Noted :
[19 empty] | + | Area roof2 = |  | C2 | 0.9 | C = | 0.9 | For Roof
[19 empty] | + | Area Road1 = |  | C3 | 0.85 | C = | 0.85 | For Pavement Road
[20 empty] | Area Road2 = |  | C4 | 0.85 | C = | 0.25 | For Lawn
|  | Drainage Capacity Required Q i = A I C = | [8 empty] | 889.11 |  |  | m3/hr.
2 |  | Gutter Discharge Capacity Calcalations
|  |  |  | Manning Equations : |  |  |  |  | Qo= | (1/h)AR2/3S1/2
|  |  |  | When : |  | h : | Rougheness Surface Coefficient
[6 empty] | h = | 0.016 For concrete or asphaltic orcast Iron
[6 empty] | h = | 0.009 For pvc or glass or plastic
[6 empty] | h = | 0.012 For welded steel and wrought Iron
[6 empty] | h = | 0.015 For cast Iron uncoated pipe
[6 empty] | h = | 0.024 For corrugate metal sheet
[6 empty] | h = | 0.011 For asbestos
2.1 |  |  | Input |  | h = | 0.016
2.2 |  |  | Gutter Width b = |  |  |  | 500 |  |  | Gutter Total Depth d = |  |  |  |  | 675
2.3 |  |  | Pipe Slope 1 : |  |  | 500
free broad=50mm.
2.4 |  |  | Assume Q max |  |  | when Normal Depth y n |  |  |  |  | = | 625 |  |  |  |  | then yn=d-50mm.
2.5 |  |  | Surface Width |  |  | B = | 500 |  |  |  | or B = |  | 0.5 |  | m.
2.6 |  |  | Gutter Discharge Cross-Area A = | [6 empty] | 0.3125 |  | m2
2.7 |  |  | Wetted Perimeter W = |  |  |  |  | 1.75 |  | m.
2.8 |  |  | Hydrualic Radius R = |  |  |  |  | 0.17857 |  | m. | [9 empty] | 375 | 5928
2.9 |  |  | Discharge Capacity Q 0 = | [6 empty] | 0.27698 |  | m3/sec.
2.1 |  |  | Discharge Velocity Vo = | [5 empty] | 0.88635 |  | m/sec. |  |  |  |  | ok. | > 0.60 m/s OK |  |  |  |  | 120
2.11 |  |  | Safety Factor S.F.= |  |  |  | 1
2.12 |  | Gutter Discharge "Net Capacity" Q n= | [7 empty] | 997.1386 |  | m3/hr.
[10 empty] | > | Q i= | 889.11 |  | m3/hr. |  | ok.
3 |  | Check critical depth for Hydrualic jump Qc | [8 empty] | from Qc2 = A3g / B
[11 empty] | or yc=(Q02*B/g)^(1/3)/b | [10 empty] | -0.9
1300
3.1 |  | Calculations Qc = |  |  |  | 0.77356 |  | m3/sec. |  | > | Q0= | 0.27698 |  | m3/sec. |  | ok. | [5 empty] | 650
|  | Calculations yc = |  |  |  | 0.31515 |  | m. |  | < | yn= | 0.625 |  | m. |  | ok.
3.2 |  | Noted :
|  |  |  | Qc | = | Q0 |  | Then Critical-flow
|  |  | or | ( yc | = | yn )
|  |  |  | Qc | > | Q0 |  | Then Sub-Critical-flow | [5 empty] | "Preferable"
|  |  | or | ( yc | < | yn )
|  |  |  | Qc | < | Q0 |  | Then Supper-Critical-flow
|  |  | or | ( yc | > | yn )

## end11
Project |  |  |  | Haffale | [11 empty] | Sheet No.
Subject |  |  |  | Site Drainage Routes A5 | [11 empty] | Project No.
| Design By |  |  |  | Narate |  |  | Checked by |  |  | Jadsada |  |  |  |  | Date |  | Feb, 09
Summary Rectangular Drainage Calculations
Item |  | Details | [14 empty] | Remarks
Reference
1
+
+
+
[19 empty] | + | Area roof &Road = | 11594 | C1 | 0.9 | Noted :
[19 empty] | + | Area roof2 = |  | C2 | 0.9 | C = | 0.9 | For Roof
[19 empty] | + | Area Road1 = |  | C3 | 0.85 | C = | 0.85 | For Pavement Road
[20 empty] | Area Road2 = |  | C4 | 0.85 | C = | 0.25 | For Lawn
|  | Drainage Capacity Required Q i = A I C = | [8 empty] | 1217.295 |  |  | m3/hr.
2 |  | Gutter Discharge Capacity Calcalations
|  |  |  | Manning Equations : |  |  |  |  | Qo= | (1/h)AR2/3S1/2
|  |  |  | When : |  | h : | Rougheness Surface Coefficient
[6 empty] | h = | 0.016 For concrete or asphaltic orcast Iron
[6 empty] | h = | 0.009 For pvc or glass or plastic
[6 empty] | h = | 0.012 For welded steel and wrought Iron
[6 empty] | h = | 0.015 For cast Iron uncoated pipe
[6 empty] | h = | 0.024 For corrugate metal sheet
[6 empty] | h = | 0.011 For asbestos | [13 empty] | -1.05
2.1 |  |  | Input |  | h = | 0.016
2.2 |  |  | Gutter Width b = |  |  |  | 500 |  |  | Gutter Total Depth d = |  |  |  |  | 900
2.3 |  |  | Pipe Slope 1 : |  |  | 400
free broad=50mm.
2.4 |  |  | Assume Q max |  |  | when Normal Depth y n |  |  |  |  | = | 850 |  |  |  |  | then yn=d-50mm.
2.5 |  |  | Surface Width |  |  | B = | 500 |  |  |  | or B = |  | 0.5 |  | m.
2.6 |  |  | Gutter Discharge Cross-Area A = | [6 empty] | 0.425 |  | m2
2.7 |  |  | Wetted Perimeter W = |  |  |  |  | 2.2 |  | m.
2.8 |  |  | Hydrualic Radius R = |  |  |  |  | 0.19318 |  | m. | [9 empty] | 375 | 5928
2.9 |  |  | Discharge Capacity Q 0 = | [6 empty] | 0.44383 |  | m3/sec.
2.1 |  |  | Discharge Velocity Vo = | [5 empty] | 1.0443 |  | m/sec. |  |  |  |  | ok. | > 0.60 m/s OK |  |  |  |  | 120
2.11 |  |  | Safety Factor S.F.= |  |  |  | 1
2.12 |  | Gutter Discharge "Net Capacity" Q n= | [7 empty] | 1597.7873 |  | m3/hr.
[10 empty] | > | Q i= | 1217.295 |  | m3/hr. |  | ok.
3 |  | Check critical depth for Hydrualic jump Qc | [8 empty] | from Qc2 = A3g / B
[11 empty] | or yc=(Q02*B/g)^(1/3)/b | [10 empty] | -0.9
1300
3.1 |  | Calculations Qc = |  |  |  | 1.2269 |  | m3/sec. |  | > | Q0= | 0.44383 |  | m3/sec. |  | ok. | [5 empty] | 650
|  | Calculations yc = |  |  |  | 0.43155 |  | m. |  | < | yn= | 0.85 |  | m. |  | ok.
3.2 |  | Noted :
|  |  |  | Qc | = | Q0 |  | Then Critical-flow
|  |  | or | ( yc | = | yn )
|  |  |  | Qc | > | Q0 |  | Then Sub-Critical-flow | [5 empty] | "Preferable"
|  |  | or | ( yc | < | yn )
|  |  |  | Qc | < | Q0 |  | Then Supper-Critical-flow
|  |  | or | ( yc | > | yn )

## trash
Project |  |  |  | Haffale | [11 empty] | Sheet No.
Subject |  |  |  | Site Drainage Routes A5 | [11 empty] | Project No.
| Design By |  |  |  | Narate |  |  | Checked by |  |  | Jadsada |  |  |  |  | Date |  | Feb, 09
Summary Rectangular Drainage Calculations
Item |  | Details | [14 empty] | Remarks
Reference
1
+
+
+
[19 empty] | + | Area roof &Road = | 11594 | C1 | 0.9 | Noted :
[19 empty] | + | Area roof2 = |  | C2 | 0.9 | C = | 0.9 | For Roof
[19 empty] | + | Area Road1 = |  | C3 | 0.85 | C = | 0.85 | For Pavement Road
[20 empty] | Area Road2 = |  | C4 | 0.85 | C = | 0.25 | For Lawn
|  | Drainage Capacity Required Q i = A I C = | [8 empty] | 1761.975 |  |  | m3/hr.
2 |  | Gutter Discharge Capacity Calcalations
|  |  |  | Manning Equations : |  |  |  |  | Qo= | (1/h)AR2/3S1/2
|  |  |  | When : |  | h : | Rougheness Surface Coefficient
[6 empty] | h = | 0.016 For concrete or asphaltic orcast Iron
[6 empty] | h = | 0.009 For pvc or glass or plastic
[6 empty] | h = | 0.012 For welded steel and wrought Iron
[6 empty] | h = | 0.015 For cast Iron uncoated pipe
[6 empty] | h = | 0.024 For corrugate metal sheet
[6 empty] | h = | 0.011 For asbestos | [13 empty] | -1.05
2.1 |  |  | Input |  | h = | 0.016
2.2 |  |  | Gutter Width b = |  |  |  | 550 |  |  | Gutter Total Depth d = |  |  |  |  | 900
2.3 |  |  | Pipe Slope 1 : |  |  | 400
free broad=50mm.
2.4 |  |  | Assume Q max |  |  | when Normal Depth y n |  |  |  |  | = | 850 |  |  |  |  | then yn=d-50mm.
2.5 |  |  | Surface Width |  |  | B = | 550 |  |  |  | or B = |  | 0.55 |  | m.
2.6 |  |  | Gutter Discharge Cross-Area A = | [6 empty] | 0.4675 |  | m2
2.7 |  |  | Wetted Perimeter W = |  |  |  |  | 2.25 |  | m.
2.8 |  |  | Hydrualic Radius R = |  |  |  |  | 0.20778 |  | m. | [9 empty] | 375 | 5928
2.9 |  |  | Discharge Capacity Q 0 = | [6 empty] | 0.5125 |  | m3/sec.
2.1 |  |  | Discharge Velocity Vo = | [5 empty] | 1.0963 |  | m/sec. |  |  |  |  | ok. | > 0.60 m/s OK |  |  |  |  | 120
2.11 |  |  | Safety Factor S.F.= |  |  |  | 1
2.12 |  | Gutter Discharge "Net Capacity" Q n= | [7 empty] | 1845.0163 |  | m3/hr.
[10 empty] | > | Q i= | 1761.975 |  | m3/hr. |  | ok.
3 |  | Check critical depth for Hydrualic jump Qc | [8 empty] | from Qc2 = A3g / B
[11 empty] | or yc=(Q02*B/g)^(1/3)/b | [10 empty] | -0.9
1300
3.1 |  | Calculations Qc = |  |  |  | 1.3496 |  | m3/sec. |  | > | Q0= | 0.5125 |  | m3/sec. |  | ok. | [5 empty] | 650
|  | Calculations yc = |  |  |  | 0.44575 |  | m. |  | < | yn= | 0.85 |  | m. |  | ok.
3.2 |  | Noted :
|  |  |  | Qc | = | Q0 |  | Then Critical-flow
|  |  | or | ( yc | = | yn )
|  |  |  | Qc | > | Q0 |  | Then Sub-Critical-flow | [5 empty] | "Preferable"
|  |  | or | ( yc | < | yn )
|  |  |  | Qc | < | Q0 |  | Then Supper-Critical-flow
|  |  | or | ( yc | > | yn )

## gravel2
Project |  |  |  | Haffale | [11 empty] | Sheet No.
Subject |  |  |  | Site Drainage Routes A5 | [11 empty] | Project No.
| Design By |  |  |  | Narate |  |  | Checked by |  |  | Jadsada |  |  |  |  | Date |  | Feb, 09
Summary Rectangular Drainage Calculations
Item |  | Details | [14 empty] | Remarks
Reference
1
+
+
+
[19 empty] | + | Area roof &Road = | 11594 | C1 | 0.9 | Noted :
[19 empty] | + | Area roof2 = |  | C2 | 0.9 | C = | 0.9 | For Roof
[19 empty] | + | Area Road1 = |  | C3 | 0.85 | C = | 0.85 | For Pavement Road
[20 empty] | Area Road2 = |  | C4 | 0.85 | C = | 0.25 | For Lawn
|  | Drainage Capacity Required Q i = A I C = | [8 empty] | 207 |  |  | m3/hr.
2 |  | Gutter Discharge Capacity Calcalations
|  |  |  | Manning Equations : |  |  |  |  | Qo= | (1/h)AR2/3S1/2
|  |  |  | When : |  | h : | Rougheness Surface Coefficient
[6 empty] | h = | 0.016 For concrete or asphaltic orcast Iron
[6 empty] | h = | 0.009 For pvc or glass or plastic
[6 empty] | h = | 0.012 For welded steel and wrought Iron
[6 empty] | h = | 0.015 For cast Iron uncoated pipe
[6 empty] | h = | 0.024 For corrugate metal sheet
[6 empty] | h = | 0.011 For asbestos
2.1 |  |  | Input |  | h = | 0.016
2.2 |  |  | Gutter Width b = |  |  |  | 300 |  |  | Gutter Total Depth d = |  |  |  |  | 650
[21 empty] | 0.72 |  | -70
2.3 |  |  | Pipe Slope 1 : |  |  | 250
No free broad
2.4 |  |  | Assume Q max |  |  | when Normal Depth y n |  |  |  |  | = | 600
2.5 |  |  | Surface Width |  |  | B = | 300 |  |  |  | or B = |  | 0.3 |  | m.
2.6 |  |  | Gutter Discharge Cross-Area A = | [6 empty] | 0.18 |  | m2
2.7 |  |  | Wetted Perimeter W = |  |  |  |  | 1.5 |  | m.
2.8 |  |  | Hydrualic Radius R = |  |  |  |  | 0.12 |  | m. | [9 empty] | 375 | 5928
2.9 |  |  | Discharge Capacity Q 0 = | [6 empty] | 0.1731 |  | m3/sec.
2.1 |  |  | Discharge Velocity Vo = | [5 empty] | 0.96168 |  | m/sec. |  |  |  |  | ok. | > 0.60 m/s OK |  |  |  |  | 120
2.11 |  |  | Safety Factor S.F.= |  |  |  | 1
2.12 |  | Gutter Discharge "Net Capacity" Q n= | [7 empty] | 623.169 |  | m3/hr.
[10 empty] | > | Q i= | 207 |  | m3/hr. |  | ok.
3 |  | Check critical depth for Hydrualic jump Qc | [8 empty] | from Qc2 = A3g / B
[11 empty] | or yc=(Q02*B/g)^(1/3)/b | [10 empty] | -0.9
1300
3.1 |  | Calculations Qc = |  |  |  | 0.43657 |  | m3/sec. |  | > | Q0= | 0.1731 |  | m3/sec. |  | ok. | [5 empty] | 650
|  | Calculations yc = |  |  |  | 0.32383 |  | m. |  | < | yn= | 0.6 |  | m. |  | ok.
3.2 |  | Noted :
|  |  |  | Qc | = | Q0 |  | Then Critical-flow
|  |  | or | ( yc | = | yn )
|  |  |  | Qc | > | Q0 |  | Then Sub-Critical-flow | [5 empty] | "Preferable"
|  |  | or | ( yc | < | yn )
|  |  |  | Qc | < | Q0 |  | Then Supper-Critical-flow
|  |  | or | ( yc | > | yn )