## SIMPLE COLUMN
ECG |  |  | Project Name |  |  |  | Job Ref. |  | (D.L+L.L)
Engineering Consultants Group |  |  | CHECKING AND PACKING HALL | [5 empty] | (D.L+L.L+W)
Bldg. 2, Block 10, El Sefarat District |  |  | Calc. By | Date | Checked By | Date | Rev. |  | St.37 | 1.4 | 6.5e-05
P.O.Box No. 1167, Cairo 11511, Egypt. |  |  | M.Nour |  |  |  | Sheet No. |  | St.44
COLUMN ID :- | ( SC-2 ) | [7 empty] | St.52
[9 empty] | IPE | AREA | h | b | s | t | r1 | h-2c | Ix | Sx | rx | Iy | ry
DESIGN CASE :- | (D.L+L.L) | a |  |  | Steel grade | St.37 |  |  | IPE 140 | 16.4 | 140 | 73 | 4.7 | 6.9 | 7 | 112.2 | 541 | 77.3 | 5.74 | 44.9 | 1.65
[5 empty] | Fy | = | 2.4 | t/cm2 | IPE 160 | 20.1 | 160 | 82 | 5 | 7.4 | 9 | 127.2 | 869 | 109 | 6.58 | 68.3 | 1.84
1)- APPLIED FORCES :- |  |  |  |  | Fu | = | 3.6 | t/cm2 | IPE 180 | 23.9 | 180 | 91 | 5.3 | 8 | 9 | 146 | 1320 | 146 | 7.42 | 101 | 2.05
Mx | = | 10 | mt | [5 empty] | IPE 200 | 28.5 | 200 | 100 | 5.6 | 8.5 | 12 | 159 | 1940 | 194 | 8.26 | 142 | 2.24
N | = | 11 | t | [5 empty] | IPE 220 | 33.4 | 220 | 110 | 5.9 | 9.2 | 12 | 177.6 | 2770 | 252 | 9.11 | 205 | 2.48
[9 empty] | IPE 240 | 39.1 | 240 | 120 | 6.2 | 9.8 | 15 | 190.4 | 3890 | 324 | 9.97 | 284 | 2.69
[9 empty] | IPE 270 | 45.9 | 270 | 135 | 6.6 | 10.2 | 15 | 219.6 | 5790 | 429 | 11.2 | 420 | 3.02
[9 empty] | IPE 300 | 53.8 | 300 | 150 | 7.1 | 10.7 | 15 | 248.6 | 8360 | 557 | 12.5 | 604 | 3.35
2)-DIM. OF SECTION :- | [8 empty] | IPE 330 | 62.6 | 330 | 160 | 7.5 | 11.5 | 18 | 271 | 11770 | 713 | 13.7 | 788 | 3.55
The section is | IPE 400 | [7 empty] | IPE 360 | 72.7 | 360 | 170 | 8 | 12.7 | 18 | 298.6 | 16270 | 904 | 15 | 1040 | 3.79
bFL.U | = | 180 | mm | [5 empty] | IPE 400 | 84.5 | 400 | 180 | 8.6 | 13.5 | 21 | 331 | 23130 | 1160 | 16.5 | 1320 | 3.95
tFL.U | = | 13.5 | mm | [5 empty] | IPE 450 | 98.8 | 450 | 190 | 9.4 | 14.6 | 21 | 378.8 | 33740 | 1500 | 18.5 | 1680 | 4.12
hWEB | = | 400 | mm | [5 empty] | IPE 500 | 116 | 500 | 200 | 10.2 | 16 | 21 | 426 | 48200 | 1930 | 20.4 | 2140 | 4.31
tWEB | = | 8.6 | mm | [5 empty] | IPE 550 | 134 | 550 | 210 | 11.1 | 17.2 | 24 | 467.6 | 67120 | 2440 | 22.3 | 2670 | 4.45
bFL.L | = | 180 | mm | [5 empty] | IPE 600 | 156 | 600 | 220 | 12 | 19 | 24 | 514 | 92080 | 3070 | 24.3 | 3390 | 4.66
tFL.L | = | 13.5 | mm
70.1854
3)-COLUMN DATA :- | [8 empty] | a | = | 0.57144 | 71.8423
Total length of column = |  | 2.5 | m | [8 empty] | 70.1854
Lu act.of comp. Flange = |  | 2.5 | m | [5 empty] | ψ | = | -0.73761 | 97.1526
Length subject to buckling in plan = |  | 2.5 | m | [8 empty] | 91.5132
Length subject to buckling out plan = |  | 2.5 | m | [8 empty] | 97.1526
Girts spacing = |  | 2.5 | m | [8 empty] | Non compact
4)- PROPERTIES OF SECTION :-
Y | = | 200 | cm
A | = | 84.5 | cm2
Ix | = | 23130 | cm4
Iy | = | 1320 | cm4
Sx | = | 1160 | cm3
rx | = | 16.5 | cm
ry | = | 3.95 | cm
5)- CHECK COMPACTNESS :-
dw/tw | = | 38.4884 | Compact
c/tf | = | 6.6667 | Compact
The sec is | Compact | [10 empty] | yes
no
6)- CHECK STRESSES :-
fbcx | = | 0.86207 | t/cm2
fca | = | 0.13018 | t/cm2
Cb | = | 1.3
Lumax | = | ( 20.bf ) / (√ fy ) = |  |  | 2.3238 | m | 2.3238 | m |  |  |  | Fltb1 | = | 1.392 | t/cm2 | Iflange | = | 656.8067 | cm4
|  | ( 1380.Af ) / ( fy.d ) x Cb = |  |  | 4.5411 | m | [5 empty] | Aflange | = | 30.0333 | cm2 | Rt | = | 4.6765 | cm
| (Lateral torsional buckling of comp.flange |  |  |  | There is L.T.B | [6 empty] | Lu/Rt | = | 53.4593 |  | 61.8223 | 138.3643
Fltb | = | 1.392 | t/cm2 |  | Use Knee Bracing |  | no |  |  |  |  | F1 | = | 1.392 | t/cm2
Fbcx | = | 1.392 | t/cm2 | [8 empty] | F2 | = | 1.392 | t/cm2
[12 empty] | F3 | = | 1.392 | t/cm2
[12 empty] | Fltb2 | = | 1.392 | t/cm2
Kin | = | 2 | E.C.O.P (P.53) | [8 empty] | Fltb | = | 1.392 | t/cm2
Kout | = | 1
Lbin | = | 5 | m | [8 empty] | Fsec | = | 1.536 | t/cm2
Lbout | = | 2.5 | m
lin | = | 30.303
lout | = | 63.2911
|  |  | lmax | = | 63.2911 | < 180 | SAFE
fc | = | 1.1396 | t/cm2
fca / fc | = | 0.11423
A1 | = | 1.00
APPLYING THE INTERACTION EQUATION :
( fca / fc ) + ( fbcx / Fbcx ) A1 = |  | 0.73353 | < | 1 |  |  | SAFE
X
Y
Mx
bFL.U
X
Mx
Y