## LF Hand Calculations
Source/Grid Data
Source Voltage | 33 | kV |  |  |  | PU source
Source Freq | 50 | Hz |  |  |  | PU source
[6 empty] | Z | #VALUE! | X | #VALUE! | R | #VALUE! | x/R | #VALUE!
Source Fault | 31.5 | kA | At | 33 | kV | PU trf
| 1800.4668 | MVA |  |  |  | Z | 0 | X | 0 | R | 0 | #DIV/0!
Source X/R | 14 |  |  |  |  | PU TOTAL
[6 empty] | Z | #VALUE! | X | #VALUE! | R | #VALUE! | x/R | #VALUE!
Base MVA | 100 | MVA
Transformer Data
Number Of Transfo | 1 | Nos
Transfo MVA | 15 | MVA
Transfo Z % | 10 | % | %X = | 9.9856 | %
Transfo X/R | 18.6 |  | %R = | 0.53686 | %
Transfo Volt Ratio
Primary | 33 | kV
Sec | 11 | kV
Transfo Primary Tap | 100 | % | So, if +2.5% tap is applied on primary side, you can enter 102.5%
| 0 | %
Calc
Load Data
Type | 100 | %Motor | 0 | % Static
S | 12 | MVA
Power Factor | 0.8
P | 9.6 | MW | (kW = kVA * CosØ)
Q | 7.2 | MVAR | (Q = Sqrt (S2-P2))
Nominal kV (Bus kV)
Primary | 33
Sec | 11
New Ratio and Base kV |  |  |  | %Z, %X and %R at New Base kV and Base MVA
Primary | 33 |  |  | %Z | 66.6667 | %
Sec | 11 |  |  | %X | 66.5705 | %
|  |  |  | %R | 3.5791 | %
Rpu | Xpu | Ppu | Qpu | Spu | Vspu | delta V | Vrpu | delta(RAD) | delta degree | %V DROP | MW loss | Mvar Loss
(Adj)
0.035791 | 0.66571 | #VALUE! | #VALUE! | #VALUE! | 1 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
(Vs-Vr)
LOAD FLOW DETAILS
P Sending | #VALUE! | MW | P receiving | #VALUE! | MW
Q Sending | #VALUE! | Mvar | Q receiving | #VALUE! | Mvar
Power Factor | #VALUE! |  | Power Factor | #VALUE!
V sending | 33 | kV | V receiving | #VALUE! | kV
V sending | 1 | PU | V receiving | #VALUE! | PU

## LF Hand Calculations (2) (hidden)
Source/Grid Data
Source Voltage | 1 | PU |  |  |  | SHORT CIRCUIT CALC
Source Freq | 50 | Hz |  |  |  | PU source
[6 empty] | Z | 0.061234 | X | 0.061098 | R | 0.0040823 | x/R | 14.9666
Source Fault | 31.5 | kA | At | 33 | kV | PU trf
| 1800.4668 | MVA |  |  |  | Z | 0.73394 | X | 0.73298 | R | 0.037446 | 19.5745
Source X/R | 14 |  |  |  |  | PU TOTAL
[6 empty] | Z | 0.79517 | X | 0.79408 | R | 0.041528 | x/R | 19.1215
Base MVA | 100 | MVA |  | Load DATA
Transformer Data
Number Of Transfo | 1 | Nos |  | Type | 80 | %IM | 20 | % STATIC
Transfo MVA | 15 | MVA |  | S | 15 | MVA
Transfo Z % | 10 | % |  | pf | 0.8
Transfo X/R | 18.6 |  |  | P | 12 | MW
Transfo Volt Ratio |  |  |  | Q | 9 | MVAR
Primary | 33 | kV
Sec | 11.55 | kV
Transfo Primary Tap | 100 | %
| 0 | % |  | OLD BASE kV |  | NOMINAL kV |  | Old Base X & R
| Calc |  |  | Primary | 33 | Primary | 33 | % X | 9.9856 | %
|  |  |  | Sec | 11.55 | Sec | 11 | % R | 0.53686 | %
Source Voltage | 33 | kV | [5 empty] | % Z | 10 | %
Calc
NEW RATIO & BASE kV |  |  |  | New Base X & R
Primary | 31.4286 |  |  | % X | 11.0091 | %
Sec | 11 |  |  | % R | 0.59189 | %
Rpu | Xpu | Ppu | Qpu | Spu | Vspu | delta V | Vrpu | delta(RAD) | delta degree | %V DROP | MW loss | Mvar Loss
(Adj)
0.039459 | 0.73394 | #VALUE! | #VALUE! | #VALUE! | 1.05 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
LOAD FLOW DETAILS
P sending | #VALUE! | MW | P receiving | #VALUE! | MW
Q sending | #VALUE! | Mvar | Q receiving | #VALUE! | Mvar
pf | #VALUE! |  | pf | #VALUE!
V sending | 33 | kV | V receiving | #VALUE! | kV
V sending | 1 | PU | V receiving | #VALUE! | PU

## SC Hidden (hidden)
Source/Grid Data
Source Voltage | 1 | PU |  |  |  | SHORT CIRCUIT CALC
Source Freq | 50 | Hz |  |  |  | PU source
[6 empty] | Z | 0.061234 | X | 0.061098 | R | 0.0040823 | x/R | 14.9666
Source Fault | 31.5 | kA | At | 33 | kV | PU trf
| 1800.4668 | MVA |  |  |  | Z | 0.73394 | X | 0.73298 | R | 0.037446 | 19.5745
Source X/R | 14 |  |  |  |  | PU TOTAL
[6 empty] | Z | 0.79517 | X | 0.79408 | R | 0.041528 | x/R | 19.1215
Base MVA | 100 | MVA |  | Load DATA
Transformer Data
Number Of Transfo | 1 | Nos |  | Type | 80 | %IM | 20 | % STATIC
Transfo MVA | 15 | MVA |  | S | 15 | MVA
Transfo Z % | 10 | % |  | pf | 0.8
Transfo X/R | 18.6 |  |  | P | 12 | MW
Transfo Volt Ratio |  |  |  | Q | 9 | MVAR
Primary | 33 | kV
Sec | 11.55 | kV
Transfo Primary Tap | 100 | % | 132
| 0 | % |  | OLD BASE kV |  | NOMINAL kV |  | Old Base X & R
| Calc |  |  | Primary | 33 | Primary | 33 | % X | 9.9856 | %
|  |  |  | Sec | 11.55 | Sec | 11 | % R | 0.53686 | %
Source Voltage | 33 | kV | [5 empty] | % Z | 10 | %
| Calc |  | 7.2607 |  | 7.2607 | 1
|  |  | 18.9806 |  | 18.9806
NEW RATIO & BASE kV |  |  |  | New Base X & R
Primary | 31.4286 |  |  | % X | 11.0091 | %
Sec | 11 |  |  | % R | 0.59189 | %
Rpu | Xpu | Ppu | Qpu | Spu | Vspu | delta V | Vrpu | delta(RAD) | delta degree | %V DROP | MW loss | Mvar Loss
(Adj)
0.039459 | 0.73394 | #VALUE! | #VALUE! | #VALUE! | 1.05 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
LOAD FLOW DETAILS
P sending | #VALUE! | MW | P receiving | #VALUE! | MW
Q sending | #VALUE! | Mvar | Q receiving | #VALUE! | Mvar
pf | #VALUE! |  | pf | #VALUE!
V sending | 33 | kV | V receiving | #VALUE! | kV
V sending | 1 | PU | V receiving | #VALUE! | PU
SHORT CIRCUIT DETAILS
Ik" Short Circuit kA | 6.6006 | kA | at | 11 | k V | AT | Net X/R | 19.1215 | Tau | 60.8657
Ip Short Circuit kA peak | 17.2551 | kAp | Ratio Ip/Ik" | 2.6142
IEC Factor | 1.1
IEC Ik" Short Circuit kA | 7.2607 | kA
Ip Short Circuit kA peak | 18.9806 | kAp | Ratio Ip/Ik" | 2.6142