## Column ROLLED
ECG |  |  | Project Name |  |  |  | Job Ref. |  | St.37 |  | Hinged
Engineering Consultants Group |  |  | CHECKING AND PACKING HALL | [5 empty] | St.44 |  | Fixed
Bldg. 2, Block 10, El Sefarat District |  |  | Calc. By | Date | Checked By | Date | Rev. |  | St.52
P.O.Box No. 1167, Cairo 11511, Egypt. |  |  | M.Nour |  |  |  | Sheet No. |  | 2.1 | 0.000135
COLUMN ID :- | ( C-2 ) | [8 empty] | AREA | h | b | s | t | r1 | h-2c | Ix | Sx | rx | Iy | Sy | ry
[9 empty] | IPE 140 | 16.4 | 140 | 73 | 4.7 | 6.9 | 7 | 112.2 | 541 | 77.3 | 5.74 | 44.9 | 12.3 | 1.65
DESIGN CASE :- | (D.L+L.L) | a |  |  | Steel grade | St.52 |  |  | IPE 160 | 20.1 | 160 | 82 | 5 | 7.4 | 9 | 127.2 | 869 | 109 | 6.58 | 68.3 | 16.7 | 1.84
[5 empty] | Fy | = | 3.6 | t/cm2 | IPE 180 | 23.9 | 180 | 91 | 5.3 | 8 | 9 | 146 | 1320 | 146 | 7.42 | 101 | 22.2 | 2.05
1)- APPLIED FORCES :- |  |  |  |  | Fu | = | 5.2 | t/cm2 | IPE 200 | 28.5 | 200 | 100 | 5.6 | 8.5 | 12 | 159 | 1940 | 194 | 8.26 | 142 | 28.5 | 2.24
Mx1 | = | 10 | mt | [5 empty] | IPE 220 | 33.4 | 220 | 110 | 5.9 | 9.2 | 12 | 177.6 | 2770 | 252 | 9.11 | 205 | 37.3 | 2.48
Mx2 | = | 0 | mt | if Mx2 at the other side put -ve sign |  |  |  |  | IPE 240 | 39.1 | 240 | 120 | 6.2 | 9.8 | 15 | 190.4 | 3890 | 324 | 9.97 | 284 | 47.3 | 2.69
My | = | 0 | mt | [5 empty] | IPE 270 | 45.9 | 270 | 135 | 6.6 | 10.2 | 15 | 219.6 | 5790 | 429 | 11.2 | 420 | 62.2 | 3.02
N | = | 100 | t | [5 empty] | IPE 300 | 53.8 | 300 | 150 | 7.1 | 10.7 | 15 | 248.6 | 8360 | 557 | 12.5 | 604 | 80.5 | 3.35
[9 empty] | IPE 330 | 62.6 | 330 | 160 | 7.5 | 11.5 | 18 | 271 | 11770 | 713 | 13.7 | 788 | 98.5 | 3.55
2)-DIM. OF SECTION :- | [8 empty] | IPE 360 | 72.7 | 360 | 170 | 8 | 12.7 | 18 | 298.6 | 16270 | 904 | 15 | 1040 | 123 | 3.79
The section is Rolled section |  | HEB 340 | [6 empty] | IPE 400 | 84.5 | 400 | 180 | 8.6 | 13.5 | 21 | 331 | 23130 | 1160 | 16.5 | 1320 | 146 | 3.95
bFL.U | = | 300 | mm | [5 empty] | IPE 450 | 98.8 | 450 | 190 | 9.4 | 14.6 | 21 | 378.8 | 33740 | 1500 | 18.5 | 1680 | 176 | 4.12
tFL.U | = | 21.5 | mm | [5 empty] | IPE 500 | 116 | 500 | 200 | 10.2 | 16 | 21 | 426 | 48200 | 1930 | 20.4 | 2140 | 214 | 4.31
hWEB | = | 340 | mm | [5 empty] | IPE 550 | 134 | 550 | 210 | 11.1 | 17.2 | 24 | 467.6 | 67120 | 2440 | 22.3 | 2670 | 254 | 4.45
tWEB | = | 12 | mm | [5 empty] | IPE 600 | 156 | 600 | 220 | 12 | 19 | 24 | 514 | 92080 | 3070 | 24.3 | 3390 | 308 | 4.66
bFL.L | = | 300 | mm
tFL.L | = | 21.5 | mm | [5 empty] | HEB 300 | 149 | 300 | 300 | 11 | 19 | 27 | 208 | 25170 | 1680 | 13 | 8560 | 571 | 7.58
[9 empty] | HEB 320 | 161 | 320 | 300 | 11.5 | 20.5 | 27 | 225 | 30820 | 1930 | 13.8 | 9240 | 616 | 7.57
| m.nour | [7 empty] | HEB 340 | 171 | 340 | 300 | 12 | 21.5 | 27 | 243 | 36660 | 2160 | 14.6 | 9690 | 646 | 7.53
3)-COLUMN DATA :- | [8 empty] | HEB 360 | 181 | 360 | 300 | 12.5 | 22.5 | 27 | 261 | 43190 | 2400 | 15.5 | 10140 | 676 | 7.49
Total length of column = |  | 5 | m | [5 empty] | HEB 400 | 198 | 400 | 300 | 13.5 | 24 | 27 | 298 | 57680 | 2880 | 17.1 | 10820 | 721 | 7.4
Lu act.of comp. Flange = |  | 5 | m | [5 empty] | HEB 450 | 218 | 450 | 300 | 14 | 26 | 27 | 344 | 79890 | 3550 | 19.1 | 11720 | 781 | 7.33
Length subject to buckling in plan = |  | 5 | m | [5 empty] | HEB 500 | 239 | 500 | 300 | 14.5 | 28 | 27 | 390 | 107200 | 4290 | 21.2 | 12620 | 842 | 7.27
Length subject to buckling out plan = |  | 5 | m | [5 empty] | HEB 550 | 254 | 550 | 300 | 15 | 29 | 27 | 438 | 136700 | 4970 | 23.2 | 13080 | 872 | 7.17
Length of girder Lg = |  | 10 | m | [5 empty] | HEB 600 | 270 | 600 | 300 | 15.5 | 30 | 27 | 486 | 171000 | 5700 | 25.2 | 13530 | 902 | 7.08
Ix (rafter) = |  | 10000 | cm4 | [5 empty] | HEB 650 | 286 | 650 | 300 | 16 | 31 | 27 | 534 | 210600 | 6480 | 27.1 | 13980 | 932 | 6.99
Base type = |  | Fixed | [6 empty] | HEB 700 | 306 | 700 | 300 | 17 | 32 | 27 | 582 | 256900 | 7340 | 29 | 14440 | 963 | 6.87
[9 empty] | HEB 800 | 334 | 800 | 300 | 17.5 | 33 | 30 | 674 | 359100 | 9890 | 32.8 | 14900 | 994 | 6.68
4)- PROPERTIES OF SECTION :- | [8 empty] | HEB 900 | 371 | 900 | 300 | 18.5 | 35 | 30 | 770 | 494100 | 10980 | 36.5 | 15820 | 1050 | 6.53
[9 empty] | HEB 1000 | 400 | 1000 | 300 | 19 | 36 | 30 | 868 | 644700 | 12890 | 40.1 | 16280 | 1090 | 6.38
A | = | 171 | cm2 | [5 empty] | (D.L+L.L)
Y | = | 170 | cm | [5 empty] | (D.L+L.L+W.L)
X | = | 150 | cm
Ix | = | 36660 | cm4 | [8 empty] | 34.8668
Iy | = | 9690 | cm4 | [5 empty] | a | = | 0.8897 | 37.6758
Sx | = | 2160 | cm3 | [8 empty] | 34.8668
Sy | = | 646 | cm3 | [5 empty] | ψ | = | 0.11628 | 47.3183
rx | = | 14.6 | cm | [8 empty] | #NUM!
ry | = | 7.53 | cm | [8 empty] | 47.3183
Compact
5)- CHECK COMPACTNESS :-
dw/tw | = | 20.25 | Web is | Compact
C/tf | = | 6.9767 | Flange is | Compact
The sec is | Compact
6)- CHECK STRESSES :-
fbcx | = | 0.46296 | t/cm2
fbcy | = | 0 | t/cm2
Fbcy | = | 2.592 | t/cm2
fca | = | 0.5848 | t/cm2
a | = | 0
Cb | = | 1.75
Lumax | = | ( 20.bf ) / (√ fy ) = |  |  | 3.1623 | m | 3.1623 | m
|  | ( 1380.Af ) / ( fy.d ) x Cb = |  |  | 12.7261 | m |  |  |  | Fltb1 | = | 2.088 | t/cm2 | Iflange | = | 4839.132 | cm4
| (Lateral torsional buckling of comp.flange) |  |  |  | There is L.T.B |  |  |  |  | Aflange | = | 71.3 | cm2 | Rt | = | 8.2383 | cm
Fltb | = | 2.088 | t/cm2 | [6 empty] | Lu/Rt | = | 60.6919 |  | 58.5662 | 131.0767
Fbcx | = | 2.088 | t/cm2 | [6 empty] | F1 | = | 2.088 | t/cm2
GA | = | 1 | (according to base type) | [6 empty] | F2 | = | 2.072 | t/cm2
GB | = | 7.332 | [7 empty] | F3 | = | 2.088 | t/cm2
K | = | 2.1 | E.C.O.P (P.61) | [6 empty] | Fltb2 | = | 2.072 | t/cm2
Lbin | = | 10.5 | m | [6 empty] | Fltb | = | 2.088 | t/cm2
Lbout | = | 5 | m | [6 empty] | Fsec | = | 2.304 | t/cm2
lin | = | 71.9178
lout | = | 66.4011
|  |  | lmax | = | 71.9178 | < 180 | SAFE
Fc | = | 1.4018 | t/cm2
fca / Fc | = | 0.41719
Cmx | = | 0.85
A1 | = | 1.4245
Cmy | = | 1
A2 | = | 1.5239
APPLYING THE INTERACTION EQUATION :
( fca / Fc ) + ( fbcx / Fbcx ) A1 +( fbcy / Fbcy ) A2 = |  |  | 0.73303 | < | 1 |  | SAFE
Mx
bFL.U
X
Y
X
Mx
Y